## Slide 1
PANGASINAN STATE UNIVERSITY | BSME-4A
WINDMILL PROJECT
PROPOSAL
A Feasibility and Siting Study
Pasuquin, Ilocos Norte, Philippines
Submitted by: Dan Mark C. Pastoral | April 29, 2026 | Engr. Marfel D. Rosario, PME
50–100 MW | 20 Turbines | Luzon Grid

## Slide 2
EXECUTIVE SUMMARY
Project Overview
Project Location
Pasuquin, Ilocos Norte, Philippines
Target Capacity
~50–100 MW (expandable)
Turbine Type
Horizontal Axis Wind Turbine (HAWT)
Estimated Turbines
15–30 units (3–5 MW each)
Grid Connection
Luzon Grid via NGCP
Project Lifespan
25–30 years
Key Benefit
Clean, renewable baseload power for Ilocos Norte

## Slide 3
SECTION II — SITE SELECTION
Why Pasuquin, Ilocos Norte?
01
High Wind Power Density
7–9 m/s average (Class 4–5). Located along Northwest Luzon Wind Corridor exposed to Northeast Monsoon (Amihan). Capacity factor: 35–45%.
02
Strategic Coastal & Hilly Terrain
Coastal plains for sea wind capture + ridge areas for high-velocity winds at altitude. Maximizes energy output per turbine.
03
Proximity to Infrastructure
Near Bangui & Burgos wind farms. NGCP transmission grid and heavy-haul routes already established in Ilocos Norte.
04
Eco-Tourism Potential
Dual purpose: power plant + tourist landmark (similar to Bangui Wind Farm). Boosts local economy and small businesses.
05
Sustainability & Energy Security
Reduces fossil fuel reliance. Wind is free and inexhaustible — hedge against volatile coal/oil prices. Supports PH climate goals.

## Slide 4
SECTION II-B — PROCESS FLOW
Wind-to-Grid Energy Flow
WIND
RESOURCE
Amihan
7–9 m/s
▶
ROTOR
BLADES
3 Blades
63.5 m each
▶
GEARBOX
1:90 ratio
1,500 RPM
▶
DFIG
GENERATOR
690 V AC
60 Hz
▶
TRANSFORMER
1
690V →
33 kV
▶
SUBSTATION
33kV
33kV →
115 kV
▶
LUZON
GRID
115 kV
~5.58 MW net
Energy Balance: Wind 13.96 MW → Aero Loss 7.68 MW → Gearbox 6.03 MW → Generator 5.85 MW → Net Grid Delivery: 5.58 MW/turbine
SCADA System
Real-time monitoring: power output, vibration, temperature, fault alarms — all 20 turbines via OPC-UA protocol
Support Systems
Pitch/yaw control • Emergency braking • Power converter • Auxiliary diesel genset (500 kVA)

## Slide 5
SECTION III — TECHNICAL SPECS
Turbine Specifications
Turbine Type
3-Bladed Horizontal Axis Wind Turbine (HAWT)
Rated Capacity
3.0 – 5.0 MW per unit
Rotor Diameter
120 – 145 meters
Hub Height
90 – 110 meters
Cut-in Wind Speed
3.0 m/s
Rated Wind Speed
12 – 14 m/s
Cut-out Wind Speed
25 m/s
Blade Material
Fiberglass-reinforced epoxy composite (GFRP)
Generator Type
Doubly Fed Induction Generator (DFIG)
Design Lifespan
25 years (with scheduled maintenance)

## Slide 6
DESIGN CONSTRAINTS
Engineering Basis & Limitations
C1
Betz Limit
Max 59.3% wind energy extractable. At V=8.5 m/s, 130m rotor → 27.7 MW available → 5.0 MW practical rated output after losses.
C2
Wake Effect Spacing
7D inline (910 m) × 4D crosswind (520 m) spacing to minimize turbulence losses between turbines.
C3
Wind Shear (Hub Ht.)
Power Law: V(100m)=8.19 m/s (+26% vs ground). Since P∝V³, this gives ~2× more power justifying 100m towers.
C4
Safety Setbacks
≥500m from residences (noise <45dB). ≥200m from coastline (storm surge buffer). Non-negotiable regulatory requirement.
C5
Grid Voltage (33 kV)
Collection at 33 kV — industry standard up to 200 MW. Step-up 3.48:1 transformer to 115 kV for NGCP Ilocos Norte grid.
C6
Foundation Loads
Overturning moment = 115,000 kN·m. Octagonal RC mat 21m wide. Safety factor = 2.30 ≥ 1.5 required. 144 anchor bolts at 65% utilization.

## Slide 7
SECTION III-A — CALCULATIONS
Key Engineering Calculations
Wind Power Density (Betz)
P = ½ × ρ × A × V³
Rotor radius (r)
65 m
Swept area (A)
13,273 m²
Air density (ρ)
1.225 kg/m³
Wind speed (V)
8.5 m/s
Available power
~27.7 MW
After Betz (×0.593)
~16.4 MW
After drivetrain losses
~11.5 MW
Practical rated output
5.0 MW ✓
Capacity Factor & Annual Energy
CF = AEP ÷ (MW × 8,760 hrs)
Rated capacity
5.0 MW
Hours/year
8,760 hrs
Max theoretical AEP
43,800 MWh/yr
Capacity factor
38%
Gross AEP/turbine
16,644 MWh/yr
Electrical losses
7% (1,165 MWh)
Net AEP/turbine
15,479 MWh/yr
Total AEP (20 units)
309,580 MWh/yr ✓

## Slide 8
SECTION IV — PLANT SITING
Site Layout & Configuration
Turbines
20 WTGs (5 rows × 4 units)
Inline spacing
7D = 910 m (wake recovery)
Cross-wind
4D = 520 m
Gross area
~9.46 km²
Setback: homes
≥500 m (noise <45dB)
Setback: coast
≥200 m (storm surge buffer)
ANCILLARY FACILITIES
Maintenance Workshop
Storage: spare parts, gearbox oil, blade tools
Control Room / SCADA
24/7 supervisory wind-farm control center
On-site Substation
33/115 kV step-up transformer + switchgear
Emergency Fire Station
Nacelle fire response, high-angle rescue
Eco-Tourism Center
Public viewing deck, exhibits — like Bangui Wind Farm

## Slide 9
SECTION V — ENVIRONMENTAL
Environmental Impact Assessment
POSITIVE IMPACTS
GHG Reduction — each 5 MW turbine avoids ~8,000–10,000 tonnes CO₂/year vs coal power
Zero direct air pollutant emissions during operation
Small physical footprint — land between turbines usable for agriculture
No water discharge; no thermal pollution to Luzon Strait
POTENTIAL IMPACTS & MITIGATION
Bird/bat mortality
Radar-based curtailment during migration season
Noise pollution
500m setback; low-noise models; quarterly monitoring
Visual/landscape
Community consultation; Bangui aesthetic branding
Shadow flicker
Model flicker zones; adjust operating hours if needed

## Slide 10
SECTION VI — FINANCIAL
Financial & Economic Analysis
CAPITAL EXPENDITURE
Wind Turbines (15–30 units)
PHP 3.0–6.0 Billion
Civil Works & Foundations
PHP 450–900 Million
Electrical & Substation
PHP 300–600 Million
Grid Connection (NGCP)
PHP 200–500 Million
Development & EIS
PHP 50–100 Million
TOTAL CAPEX
PHP 4.4–8.9 Billion
REVENUE PROJECTIONS
Installed Capacity
50–100 MW
Capacity Factor
38% average
Annual Energy Output
166–332 GWh/year
FiT Rate (ERC)
PHP 8.53/kWh
Gross Annual Revenue
PHP 1.42–2.83 Billion
Simple Payback Period
8–12 years
ECONOMIC & SOCIAL BENEFITS
50–100 permanent jobs during operations • 300–500 construction jobs
Real property tax & business tax to Pasuquin LGU • Eco-tourism revenue
Reduces fossil fuel dependence • Stabilizes long-term energy prices

## Slide 11
CONCLUSION & RECOMMENDATIONS
Key Takeaways
01
Technically Feasible
Pasuquin's Class 4–5 wind resource, 38% capacity factor, and existing NGCP infrastructure make the project viable using standard HAWT technology.
02
Economically Viable
PHP 4.4–8.9B CAPEX, PHP 8.53/kWh FiT rate, and 8–12 year simple payback period over a 25-year project life deliver strong long-term returns.
03
Environmentally Responsible
Avoids ~160,000–200,000 tonnes CO₂/year. Zero water discharge. Small footprint. Full EIS and ECC compliance with DENR and DOE.
04
Serves ~77,400 Households
Total net AEP of 309,580 MWh/year from 20 turbines. Supports PH 35% RE target by 2030 under RA 9513.
Dan Mark C. Pastoral | BSME-4A | Pangasinan State University | April 2026